## Sheet1
Product Type → Operating Mode → Installation Location → Climate → Standard → Test Condition → Auto-Load Indoor/Outdoor Design Conditions
Product Type | Operating Mode | Installation Location (Geographic) | Climate | Standard | Test Condition | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB | Notes
Air Conditioning | Cooling | North America → USA/Canada | Moderate | AHRI 340/360 | Standard Cooling Rating | 80°F / 26.7°C | 67°F / 19.4°C | 95°F / 35.0°C | 75°F / 23.9°C | Air-cooled equipment
Air Conditioning | Cooling | North America → USA/Canada | Cool / Cold | AHRI 340/360 | Low Ambient Cooling | 67°F / 19.4°C | 57°F / 13.9°C | 67°F / 19.4°C | 57°F / 13.9°C | Operating test
Air Conditioning | Cooling | North America → USA/Canada | Hot | AHRI 340/360 | Maximum Cooling | 80°F / 26.7°C | 67°F / 19.4°C | 115°F / 46.1°C | N/A | Operating limit
Heat Pump | Heating | North America → USA/Canada | Warm | AHRI 340/360 | High Temperature Heating | 70°F / 21.1°C | 60°F / 15.6°C | 47°F / 8.3°C | 43°F / 6.1°C | Heating rating
Heat Pump | Heating | North America → USA/Canada | Cold | AHRI 340/360 | Low Temperature Heating | 70°F / 21.1°C | 60°F / 15.6°C | 17°F / -8.3°C | 15°F / -9.4°C | Heating rating
Air Conditioning | Cooling | International | Moderate | AHRI International | T1 | 80.6°F / 27.0°C | 66.2°F / 19.0°C | 95°F / 35.0°C | 75.2°F / 24.0°C | Moderate climate
Air Conditioning | Cooling | International | Cool | AHRI International | T2 | 69.8°F / 21.0°C | 59°F / 15.0°C | 80.6°F / 27.0°C | 66.2°F / 19.0°C | Cool climate
Air Conditioning | Cooling | International | Hot / Tropical | AHRI International | T3 | 84.2°F / 29.0°C | 66.2°F / 19.0°C | 114.8°F / 46.0°C | 75.2°F / 24.0°C | Hot climate
Heat Pump | Heating | International | Warm | AHRI International | H1 | 68°F / 20.0°C | 59°F / 15.0°C | 44.6°F / 7.0°C | 42.8°F / 6.0°C | Warm climate
Heat Pump | Heating | International | Moderate | AHRI International | H2 | 68°F / 20.0°C | 59°F / 15.0°C | 35.6°F / 2.0°C | 33.8°F / 1.0°C | Moderate climate
Heat Pump | Heating | International | Cold | AHRI International | H3 | 68°F / 20.0°C | 59°F / 15.0°C | 19.4°F / -7.0°C | 17.6°F / -8.0°C | Cold climate
Air Conditioning / Heat Pump | Cooling | International | Moderate | ISO 5151 | T1 | 80.6°F / 27.0°C | 66.2°F / 19.0°C | 95°F / 35.0°C | 75.2°F / 24.0°C | Non-ducted AC/HP
Air Conditioning / Heat Pump | Cooling | International | Cool | ISO 5151 | T2 | 69.8°F / 21.0°C | 59°F / 15.0°C | 80.6°F / 27.0°C | 66.2°F / 19.0°C | Cool climate
Air Conditioning / Heat Pump | Cooling | International | Tropical | ISO 5151 | T3 | 84.2°F / 29.0°C | 66.2°F / 19.0°C | 114.8°F / 46.0°C | 75.2°F / 24.0°C | Tropical climate
Heat Pump | Heating | International | Warm | ISO 5151 | H1 | 68°F / 20.0°C | 59°F / 15.0°C | 44.6°F / 7.0°C | 42.8°F / 6.0°C | Heating test
Heat Pump | Heating | International | Moderate | ISO 5151 | H2 | 68°F / 20.0°C | 59°F / 15.0°C | 35.6°F / 2.0°C | 33.8°F / 1.0°C | Heating test
Heat Pump | Heating | International | Cold | ISO 5151 | H3 | 68°F / 20.0°C | 59°F / 15.0°C | 19.4°F / -7.0°C | 17.6°F / -8.0°C | Heating test
Ducted AC / Heat Pump | Cooling | International | Moderate | ISO 13253 | Standard Cooling | 80.6°F / 27.0°C | 66.2°F / 19.0°C | 95°F / 35.0°C | 75.2°F / 24.0°C | Ducted units
Ducted AC / Heat Pump | Cooling | International | Hot / Tropical | ISO 13253 | Maximum Cooling | 84.2°F / 29.0°C | 66.2°F / 19.0°C | 114.8°F / 46.0°C | 75.2°F / 24.0°C | Ducted T3
Ducted Heat Pump | Heating | International | Warm | ISO 13253 | Standard Heating | 68°F / 20.0°C | 59°F / 15.0°C | 44.6°F / 7.0°C | 42.8°F / 6.0°C | Heating rating
Ducted Heat Pump | Heating | International | Cold | ISO 13253 | Low Temperature Heating | 68°F / 20.0°C | 59°F / 15.0°C | 19.4°F / -7.0°C | 17.6°F / -8.0°C | H3 equivalent
HVAC / Heat Pump | Cooling | Europe → Applicable Country | Moderate | EN 14511 | A35 | 80.6°F / 27.0°C | 66.2°F / 19.0°C | 95°F / 35.0°C | 75.2°F / 24.0°C | EER rating
Heat Pump | Heating | Europe → Applicable Country | Warm | EN 14511 | A7 | 68°F / 20.0°C | 59°F / 15.0°C | 44.6°F / 7.0°C | 42.8°F / 6.0°C | COP rating
Heat Pump | Heating | Europe → Applicable Country | Moderate / Cold | EN 14511 | A2 | 68°F / 20.0°C | 59°F / 15.0°C | 35.6°F / 2.0°C | 33.8°F / 1.0°C | Winter rating
Heat Pump | Heating | Europe → Applicable Country | Cold | EN 14511 | A-7 | 68°F / 20.0°C | 59°F / 15.0°C | 19.4°F / -7.0°C | 17.6°F / -8.0°C | Cold climate rating

## Sheet2
Product Type | Operating Mode | Installation Location (Geographic) | Climate | Standard | Test Condition | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB | Capacity Rating | Efficiency Rating | Application Type | Unit Type | User Override Allowed | Notes
Air Conditioning | Cooling | North America → USA/Canada | Moderate | AHRI 340/360 | Standard Cooling Rating | 80°F / 26.7°C | 67°F / 19.4°C | 95°F / 35.0°C | 75°F / 23.9°C | Cooling Capacity | EER, IEER | Commercial | Ducted / Packaged | Yes | Air-cooled equipment
Air Conditioning | Cooling | North America → USA/Canada | Cool / Cold | AHRI 340/360 | Low Ambient Cooling | 67°F / 19.4°C | 57°F / 13.9°C | 67°F / 19.4°C | 57°F / 13.9°C | Operating Test | N/A | Commercial | Ducted / Packaged | Yes | Operating test
Air Conditioning | Cooling | North America → USA/Canada | Hot | AHRI 340/360 | Maximum Cooling | 80°F / 26.7°C | 67°F / 19.4°C | 115°F / 46.1°C | N/A | Operating Test | N/A | Commercial | Ducted / Packaged | Yes | Operating limit
Heat Pump | Heating | North America → USA/Canada | Warm | AHRI 340/360 | High Temperature Heating | 70°F / 21.1°C | 60°F / 15.6°C | 47°F / 8.3°C | 43°F / 6.1°C | Heating Capacity | COP | Commercial | Ducted | Yes | Heating rating
Heat Pump | Heating | North America → USA/Canada | Cold | AHRI 340/360 | Low Temperature Heating | 70°F / 21.1°C | 60°F / 15.6°C | 17°F / -8.3°C | 15°F / -9.4°C | Heating Capacity | COP | Commercial | Ducted | Yes | Heating rating
Air Conditioning | Cooling | International | Moderate | AHRI International | T1 | 80.6°F / 27°C | 66.2°F / 19°C | 95°F / 35°C | 75.2°F / 24°C | Cooling Capacity | EER | Residential / Commercial | All | Yes | Moderate climate
Air Conditioning | Cooling | International | Cool | AHRI International | T2 | 69.8°F / 21°C | 59°F / 15°C | 80.6°F / 27°C | 66.2°F / 19°C | Cooling Capacity | EER | Residential / Commercial | All | Yes | Cool climate
Air Conditioning | Cooling | International | Hot / Tropical | AHRI International | T3 | 84.2°F / 29°C | 66.2°F / 19°C | 114.8°F / 46°C | 75.2°F / 24°C | Cooling Capacity | EER | Residential / Commercial | All | Yes | Hot climate
Heat Pump | Heating | International | Warm | AHRI International | H1 | 68°F / 20°C | 59°F / 15°C | 44.6°F / 7°C | 42.8°F / 6°C | Heating Capacity | COP | Residential / Commercial | All | Yes | Warm climate
Heat Pump | Heating | International | Moderate | AHRI International | H2 | 68°F / 20°C | 59°F / 15°C | 35.6°F / 2°C | 33.8°F / 1°C | Heating Capacity | COP | Residential / Commercial | All | Yes | Moderate climate
Heat Pump | Heating | International | Cold | AHRI International | H3 | 68°F / 20°C | 59°F / 15°C | 19.4°F / -7°C | 17.6°F / -8°C | Heating Capacity | COP | Residential / Commercial | All | Yes | Cold climate
Air Conditioning / Heat Pump | Cooling | International | Moderate | ISO 5151 | T1 | 27°C | 19°C | 35°C | 24°C | Cooling Capacity | EER, COP | Residential | Non-Ducted | Yes | Non-ducted AC/HP
Air Conditioning / Heat Pump | Cooling | International | Cool | ISO 5151 | T2 | 21°C | 15°C | 27°C | 19°C | Cooling Capacity | EER | Residential | Non-Ducted | Yes | Cool climate
Air Conditioning / Heat Pump | Cooling | International | Tropical | ISO 5151 | T3 | 29°C | 19°C | 46°C | 24°C | Cooling Capacity | EER | Residential | Non-Ducted | Yes | Tropical climate
Heat Pump | Heating | International | Warm | ISO 5151 | H1 | 20°C | 15°C | 7°C | 6°C | Heating Capacity | COP | Residential | Non-Ducted | Yes | Heating test
Heat Pump | Heating | International | Moderate | ISO 5151 | H2 | 20°C | 15°C | 2°C | 1°C | Heating Capacity | COP | Residential | Non-Ducted | Yes | Heating test
Heat Pump | Heating | International | Cold | ISO 5151 | H3 | 20°C | 15°C | -7°C | -8°C | Heating Capacity | COP | Residential | Non-Ducted | Yes | Heating test
Ducted AC / Heat Pump | Cooling | International | Moderate | ISO 13253 | Standard Cooling | 27°C | 19°C | 35°C | 24°C | Cooling Capacity | EER | Commercial | Ducted | Yes | Ducted units
Ducted AC / Heat Pump | Cooling | International | Hot / Tropical | ISO 13253 | Maximum Cooling | 29°C | 19°C | 46°C | 24°C | Cooling Capacity | EER | Commercial | Ducted | Yes | Ducted T3
Ducted Heat Pump | Heating | International | Warm | ISO 13253 | Standard Heating | 20°C | 15°C | 7°C | 6°C | Heating Capacity | COP | Commercial | Ducted | Yes | Heating rating
Ducted Heat Pump | Heating | International | Cold | ISO 13253 | Low Temperature Heating | 20°C | 15°C | -7°C | -8°C | Heating Capacity | COP | Commercial | Ducted | Yes | H3 equivalent
HVAC / Heat Pump | Cooling | Europe | Moderate | EN 14511 | A35 | 27°C | 19°C | 35°C | 24°C | Cooling Capacity | EER | Residential / Commercial | All | Yes | EER rating
Heat Pump | Heating | Europe | Warm | EN 14511 | A7 | 20°C | 15°C | 7°C | 6°C | Heating Capacity | COP | Residential / Commercial | All | Yes | COP rating
Heat Pump | Heating | Europe | Moderate / Cold | EN 14511 | A2 | 20°C | 15°C | 2°C | 1°C | Heating Capacity | COP | Residential / Commercial | All | Yes | Winter rating
Heat Pump | Heating | Europe | Cold | EN 14511 | A-7 | 20°C | 15°C | -7°C | -8°C | Heating Capacity | COP | Residential / Commercial | All | Yes | Cold climate rating