# Entering Air DB/WB Condition Selection

## Refrigeration & HVAC Application Platform – Phase 1

# Purpose

The purpose of this module is to help determine the appropriate Entering Air Dry-Bulb Temperature (DB) and Entering Air Wet-Bulb Temperature (WB) for the selected product, operating mode, installation location, climate, and applicable standard.

The person using the application should not need to know the correct DB/WB values in advance.

The application should guide the professional through:

- Product Type

- Operating Mode

- Product Installation Location

- Climate

- Applicable Standard

- Rating/Test Condition

- Recommended Entering Air DB/WB

- Confirmation or Project-Specific Override

The application should clearly explain:

What value is being used → Why it was selected → Where it came from → Whether it is a standard condition or project-specific condition.

# Basic Explanation of DB and WB

Before asking the professional to enter or modify DB/WB values, the application should provide a simple explanation.

## Dry-Bulb Temperature (DB)

Dry-Bulb Temperature (DB) is the normal temperature of the air measured using a standard temperature sensor or thermometer.

Example:

80°F DB

means the air temperature is 80°F.

DB primarily describes the sensible temperature condition of the air.

## Wet-Bulb Temperature (WB)

Wet-Bulb Temperature (WB) is a temperature related to both the air temperature and the moisture content of the air.

Example:

80°F DB / 67°F WB

The:

- 80°F DB represents the air temperature.

- 67°F WB provides information about the moisture condition of the air.

WB is particularly important for air-conditioning applications because cooling coils may remove both:

- Sensible heat

- Latent heat / moisture

# Why DB and WB Are Important

### Dry-Bulb

Primarily used to describe:

- Air temperature

- Sensible cooling

- Sensible heating

- Room temperature

- Supply-air temperature

### Wet-Bulb

Used to describe the moisture condition of the air and is important for:

- Latent cooling

- Dehumidification

- Coil condensation

- Total cooling calculations

- Psychrometric calculations

Therefore:

DB + WB provide a description of the entering moist-air condition used by the air-side and psychrometric calculations.

The application should not describe WB simply as “humidity.”

WB is a temperature measurement that provides information about the moisture condition of the air.

# Entering Air vs. Leaving Air

The application must clearly distinguish between:

### Entering Air Condition

The air condition immediately before the air enters the evaporator/DX coil or other air-side heat exchanger.

Example:

80°F DB / 67°F WB

### Leaving Air Condition

The air condition after the air leaves the coil or heat exchanger.

Example:

55°F DB / 54°F WB

These are separate design parameters.

For Phase 1, the primary focus is:

Entering Air DB/WB

# Professional Workflow

The application should not immediately ask:

Enter DB = ?

Instead, it should first understand the application.

The workflow shall be:

Product Type
      ↓
Operating Mode
      ↓
Product Installation Location
      ↓
Climate
      ↓
Applicable Standard
      ↓
Rating/Test Condition
      ↓
Recommended DB/WB
      ↓
Accept or Modify
      ↓
Project Design Condition

# Step 1 – Product Type

Select the product or equipment type you are designing or selecting

Example categories:

## Air Conditioning

- DX Air Handling Unit

- Packaged Air Conditioner

- Rooftop Unit

- Ducted Split System

- Non-Ducted Split System

- Heat Pump

- Chiller

- Other

## Refrigeration

- Walk-In Cooler

- Walk-In Freezer

- Refrigerated Room

- Display Case

- Refrigeration Evaporator

- Condensing Unit

- Process Refrigeration

- Other

## Heat Pump

- Air-Source Heat Pump

- Ducted Heat Pump

- Packaged Heat Pump

- Process Heat Pump

- Other

The application should display relevant equipment types based on the selected product category.

# Step 2 – Operating Mode

### Operating Mode

- Cooling

- Heating

- Cooling & Heating

Do not use one DB/WB condition to represent both cooling and heating.

# Step 3 – Product Installation Location

The location means:

The physical location where the product/equipment will be installed or operated.

The professional selects:

### Country

Examples:

- Canada

- United States

- Mexico

- United Kingdom

- Germany

- France

- India

- Australia

- Other, etc.

Then:

### Province / State / Region

Then:

### City / Location

The location can be used to determine or recommend:

- Climate classification

- Outdoor design conditions

- Regional requirements

- Applicable standards

- Market-specific rating requirements

- Other location-dependent requirements

### Important

Location alone must not determine the applicable standard.

The application should evaluate:

Product Type + Equipment Type + Operating Mode + Installation Location + Market + Climate + Standard Scope

# Step 4 – Climate

The application should automatically determine or recommend the climate classification from the installation location.

Examples:

- Cold Climate

- Cool Climate

- Moderate Climate

- Warm Climate

- Hot Climate

- Hot-Humid Climate

- Hot-Dry Climate

- Tropical Climate

Display:

### Climate

Detected / Recommended

[ Cold Climate ▼ ]

The professional should be able to override the recommendation.

If changed:

🟠 USER OVERRIDE

# Step 5 – Applicable Standard

The application should determine the potentially applicable standard.

The logic should follow:

Product Type
      ↓
Equipment Type
      ↓
Operating Mode
      ↓
Installation Location / Market
      ↓
Climate
      ↓
Applicable Standard Database
      ↓
Recommended Standard

Example:

### Recommended Standard

AHRI XXXX

### Why?

The application recommends this standard based on the selected equipment type, operating mode, installation market/location, climate, and the scope of the standard.

The professional should be able to:

[ Accept Recommended Standard ]

or:

[ Select Different Standard ]

The application must retain the source and reason for the recommendation.

# IMPORTANT – Standard Data Acquisition

We should design the application to support two methods of obtaining standard conditions.

## Method A – Automatic Standard Data Retrieval

If an authorized and reliable source/API/database is available, the application may retrieve:

- Standard

- Edition

- Equipment scope

- Rating condition

- Indoor DB

- Indoor WB

- Outdoor DB

- Outdoor WB

- Other required test conditions

- Source

- Effective date

- Revision information

The application must not automatically trust an unverified web result.

Retrieved values should be validated and associated with a source document or authoritative source.

# Method B – Internal Standard Condition Database

If the we cannot automatically retrieve the required standard values from the source, the application must have an internal structured database containing the standard conditions.

This database becomes the application’s controlled reference database.

The developer should be able to manually enter, verify, update, and maintain standard conditions.

### Important

The database should not simply be one large table of temperatures.

It must contain relationships between:

Product Type
      ↓
Equipment Type
      ↓
Operating Mode
      ↓
Installation Market / Location
      ↓
Climate
      ↓
Applicable Standard
      ↓
Standard Edition
      ↓
Test / Rating Condition
      ↓
Entering Air Conditions
      ↓
Outdoor Conditions

# Standard Condition Master Database

Refer Excel sheet Standard DB WB Rating Conditions Database or below table

The following structure is recommended.

## 14.1 Main Standard Condition Table

| Field | Description |
| --- | --- |
| Record ID | Unique database record |
| Product Type | AC / Refrigeration / Heat Pump / etc. |
| Equipment Type | DX AHU / Rooftop / Heat Pump / etc. |
| Operating Mode | Cooling / Heating |
| Installation Country | Country |
| Installation Region | Province / State / Region |
| Climate | Climate classification |
| Applicable Standard | AHRI 340/360 / ISO 5151 / ISO 13253 / EN 14511 / etc. |
| Standard Edition | Edition/year |
| Test Condition | Standard Cooling / T1 / T2 / T3 / H1 / etc. |
| Condition Type | Rating / Maximum / Low Ambient / Operating Limit |
| Indoor DB | Entering indoor DB |
| Indoor WB | Entering indoor WB |
| Outdoor DB | Outdoor entering DB |
| Outdoor WB | Outdoor entering WB |
| DB Unit | °F / °C |
| WB Unit | °F / °C |
| Source | Document/source |
| Source URL | Source reference |
| Source Page/Section | Exact location in source |
| Verification Status | Verified / Review Required |
| Effective Date | Date applicable |
| Expiry/Replacement | If applicable |
| Notes | Engineering notes |
| Last Verified | Date |
| Verified By | Person/process |
| Database Version | Revision |

# Recommended Relational Database Structure

For a commercial application, do not put everything into one physical database table.

The developer should preferably create related tables.

### Table 1 – Product Types

| Product Type ID | Product Type |
| --- | --- |
| PT-001 | Air Conditioning |
| PT-002 | Refrigeration |
| PT-003 | Heat Pump |

### Table 2 – Equipment Types

| Equipment ID | Product Type | Equipment |
| --- | --- | --- |
| EQ-001 | PT-001 | DX AHU |
| EQ-002 | PT-001 | Rooftop Unit |
| EQ-003 | PT-003 | Air-Source Heat Pump |

### Table 3 – Operating Modes

| Mode ID | Mode |
| --- | --- |
| COOL | Cooling |
| HEAT | Heating |
| BOTH | Cooling & Heating |

### Table 4 – Locations

| Location ID | Country | Region | City |
| --- | --- | --- | --- |
| LOC-001 | Canada | Ontario | Toronto |
| LOC-002 | Canada | Alberta | Calgary |
| LOC-003 | USA | Texas | Houston |

### Table 5 – Climate

| Climate ID | Climate |
| --- | --- |
| CL-001 | Cold |
| CL-002 | Cool |
| CL-003 | Moderate |
| CL-004 | Hot |
| CL-005 | Hot-Humid |
| CL-006 | Hot-Dry |
| CL-007 | Tropical |

### Table 6 – Standards

| Standard ID | Standard | Edition | Scope | Status |
| --- | --- | --- | --- | --- |
| STD-001 | AHRI 340/360 | XXXX | Applicable equipment | Active |
| STD-002 | ISO 5151 | XXXX | Non-ducted AC/HP | Active |
| STD-003 | ISO 13253 | XXXX | Ducted AC/HP | Active |
| STD-004 | EN 14511 | XXXX | HVAC/Heat Pump | Active |

### Table 7 – Rating/Test Conditions

| Condition ID | Standard ID | Test Condition | Mode | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB |
| --- | --- | --- | --- | --- | --- | --- | --- |
| RC-001 | STD-001 | Standard Cooling | Cooling | 80°F | 67°F | 95°F | 75°F |
| RC-002 | STD-001 | Low Ambient Cooling | Cooling | 67°F | 57°F | 67°F | 57°F |
| RC-003 | STD-001 | Maximum Cooling | Cooling | 80°F | 67°F | 115°F | N/A |
| RC-004 | STD-001 | High Temp Heating | Heating | 70°F | 60°F | 47°F | 43°F |
| RC-005 | STD-001 | Low Temp Heating | Heating | 70°F | 60°F | 17°F | 15°F |

Important: These values are examples from the supplied reference dataset and must be independently verified against the applicable standard edition before being released as validated production data.

# 16. Standard Condition Database – Supplied Initial Dataset

The following dataset can be used as the initial seed/reference dataset, subject to source verification.

## 16.1 AHRI 340/360

| Product Type | Operating Mode | Climate | Standard | Test Condition | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Air Conditioning | Cooling | Applicable | AHRI 340/360 | Standard Cooling Rating | 80°F / 26.7°C | 67°F / 19.4°C | 95°F / 35°C | 75°F / 23.9°C | Air-cooled equipment |
| Air Conditioning | Cooling | Applicable | AHRI 340/360 | Low Ambient Cooling | 67°F / 19.4°C | 57°F / 13.9°C | 67°F / 19.4°C | 57°F / 13.9°C | Operating test |
| Air Conditioning | Cooling | Applicable | AHRI 340/360 | Maximum Cooling | 80°F / 26.7°C | 67°F / 19.4°C | 115°F / 46.1°C | N/A | Operating limit |
| Heat Pump | Heating | Applicable | AHRI 340/360 | High Temperature Heating | 70°F / 21.1°C | 60°F / 15.6°C | 47°F / 8.3°C | 43°F / 6.1°C | Heating rating |
| Heat Pump | Heating | Applicable | AHRI 340/360 | Low Temperature Heating | 70°F / 21.1°C | 60°F / 15.6°C | 17°F / -8.3°C | 15°F / -9.4°C | Heating rating |

# 17. AHRI International / T1-T3 / H1-H3

| Product Type | Operating Mode | Climate | Standard | Test Condition | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Air Conditioning | Cooling | Moderate | AHRI International | T1 | 80.6°F / 27°C | 66.2°F / 19°C | 95°F / 35°C | 75.2°F / 24°C | Moderate climate |
| Air Conditioning | Cooling | Cool | AHRI International | T2 | 69.8°F / 21°C | 59°F / 15°C | 80.6°F / 27°C | 66.2°F / 19°C | Cool climate |
| Air Conditioning | Cooling | Hot | AHRI International | T3 | 84.2°F / 29°C | 66.2°F / 19°C | 114.8°F / 46°C | 75.2°F / 24°C | Hot climate |
| Heat Pump | Heating | Warm | AHRI International | H1 | 68°F / 20°C | 59°F / 15°C | 44.6°F / 7°C | 42.8°F / 6°C | Warm climate |
| Heat Pump | Heating | Moderate | AHRI International | H2 | 68°F / 20°C | 59°F / 15°C | 35.6°F / 2°C | 33.8°F / 1°C | Moderate climate |
| Heat Pump | Heating | Cold | AHRI International | H3 | 68°F / 20°C | 59°F / 15°C | 19.4°F / -7°C | 17.6°F / -8°C | Cold climate |

# 18. ISO 5151

| Product Type | Operating Mode | Climate | Standard | Test Condition | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Air Conditioning / Heat Pump | Cooling | Moderate | ISO 5151 | T1 | 27°C | 19°C | 35°C | 24°C | Non-ducted AC/HP |
| Air Conditioning / Heat Pump | Cooling | Cool | ISO 5151 | T2 | 21°C | 15°C | 27°C | 19°C | Cool climate |
| Air Conditioning / Heat Pump | Cooling | Tropical | ISO 5151 | T3 | 29°C | 19°C | 46°C | 24°C | Tropical climate |
| Heat Pump | Heating | Warm | ISO 5151 | H1 | 20°C | 15°C | 7°C | 6°C | Heating test |
| Heat Pump | Heating | Moderate | ISO 5151 | H2 | 20°C | 15°C | 2°C | 1°C | Heating test |
| Heat Pump | Heating | Cold | ISO 5151 | H3 | 20°C | 15°C | -7°C | -8°C | Heating test |

# 19. ISO 13253

| Product Type | Operating Mode | Climate | Standard | Test Condition | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ducted AC/HP | Cooling | Moderate | ISO 13253 | Standard Cooling | 27°C | 19°C | 35°C | 24°C | Ducted units |
| Ducted AC/HP | Cooling | Hot | ISO 13253 | Maximum Cooling | 29°C | 19°C | 46°C | 24°C | Ducted T3 |
| Ducted Heat Pump | Heating | Warm | ISO 13253 | Standard Heating | 20°C | 15°C | 7°C | 6°C | Heating rating |
| Ducted Heat Pump | Heating | Cold | ISO 13253 | Low Temperature Heating | 20°C | 15°C | -7°C | -8°C | H3 equivalent |

# 20. EN 14511

| Product Type | Operating Mode | Climate | Standard | Test Condition | Indoor DB | Indoor WB | Outdoor DB | Outdoor WB | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| HVAC / Heat Pump | Cooling | Standard | EN 14511 | A35 | 27°C DB | 19°C WB | 35°C DB | 24°C WB | EER rating |
| Heat Pump | Heating | Standard | EN 14511 | A7 | 20°C DB | 15°C WB | 7°C DB | 6°C WB | COP rating |
| Heat Pump | Heating | Moderate | EN 14511 | A2 | 20°C DB | 15°C WB | 2°C DB | 1°C WB | Winter rating |
| Heat Pump | Heating | Cold | EN 14511 | A-7 | 20°C DB | 15°C WB | -7°C DB | -8°C WB | Cold climate rating |

# Standard Selection Engine

The application should use the database to determine the most appropriate standard.

Conceptually:

INPUT
 │
 ├── Product Type
 ├── Equipment Type
 ├── Operating Mode
 ├── Installation Location
 ├── Market
 └── Climate
       │
       ▼
STANDARD SELECTION ENGINE
       │
       ▼
FILTER APPLICABLE STANDARDS
       │
       ▼
CHECK STANDARD SCOPE
       │
       ▼
CHECK STANDARD EDITION
       │
       ▼
CHECK RATING CONDITION
       │
       ▼
RECOMMENDED STANDARD

If multiple standards are applicable, show them to the professional.

Example:

### Applicable Standards

| Standard | Applicability | Status |
| --- | --- | --- |
| AHRI 340/360 | Highly Applicable | 🟢 Recommended |
| ISO 13253 | Applicable | 🔵 Alternative |
| EN 14511 | Market dependent | 🔵 Alternative |

# Rating Condition Selection

Once the standard is selected, display available conditions.

Example:

### Select Rating/Test Condition

- Standard Cooling

- Maximum Cooling

- Low Ambient Cooling

- Standard Heating

- High Temperature Heating

- Low Temperature Heating

- T1

- T2

- T3

- H1

- H2

- H3

The available conditions must come from the selected standard/equipment database.

Do not show irrelevant conditions.

# Recommended Design Conditions

After selecting the rating/test condition, display:

# Recommended Design Conditions

## Cooling

| Air Stream | DB (°F) | DB (°C) | WB (°F) | WB (°C) | Source |
| --- | --- | --- | --- | --- | --- |
| Indoor / Entering Air | 80.0 | 26.7 | 67.0 | 19.4 | 🟣 Standard |
| Outdoor / Condenser Air | 95.0 | 35.0 | 75.0 | 23.9 | 🟣 Standard |

# Heating Design Conditions

If heating is selected:

## Heating

| Air Stream | DB (°F) | DB (°C) | WB (°F) | WB (°C) | Source |
| --- | --- | --- | --- | --- | --- |
| Indoor / Entering Air | 68.0 | 20.0 | 59.0 | 15.0 | 🟣 Standard |
| Outdoor / Entering Air | 44.6 | 7.0 | 42.8 | 6.0 | 🟣 Standard |

Only display WB when applicable to the selected standard/equipment/rating condition.

# Standard Condition vs. Project Condition

This distinction is extremely important.

## Standard Rating Condition

A standardized condition used to rate, compare, or test equipment.

Example:

80°F DB / 67°F WB

Status:

🟣 STANDARD CONDITION

## Project Design Condition

The actual condition intended for the specific installation/project.

Example:

78°F DB / 65°F WB

Status:

🔵 PROJECT CONDITION

The two conditions must exist independently.

# User/Professional Override

The professional may modify a recommended condition.

Example:

### Standard

| Parameter | Standard |
| --- | --- |
| Indoor DB | 80.6°F |
| Indoor WB | 66.2°F |
| Outdoor DB | 95°F |
| Outdoor WB | 75.2°F |

### Project

| Parameter | Project |
| --- | --- |
| Indoor DB | 80°F |
| Indoor WB | 67°F |
| Outdoor DB | 104°F |
| Outdoor WB | 78°F |

Display:

🟠 USER-DEFINED PROJECT CONDITION

# Condition Comparison

Display:

| Parameter | Standard Rating | Project Design | Status |
| --- | --- | --- | --- |
| Indoor DB | 80.6°F | 80°F | 🟠 Override |
| Indoor WB | 66.2°F | 67°F | 🟠 Override |
| Outdoor DB | 95°F | 104°F | 🟠 Override |
| Outdoor WB | 75.2°F | 78°F | 🟠 Override |

This allows the professional to immediately understand the difference between:

Rating Condition

and

Actual Project Condition

# Override Audit Trail

For every override, record:

- Project ID

- Design Case ID

- Standard

- Standard Edition

- Rating Condition

- Parameter

- Original Value

- Original Unit

- New Value

- New Unit

- Reason

- Person making change

- Date/time

- Revision

Example:

Parameter: Outdoor DB
Standard Value: 95°F
Project Value: 104°F
Reason: Project outdoor design condition
Changed By: Professional
Date: YYYY-MM-DD

# Unit Selection

Every temperature field must have its own unit selection.

Example:

Indoor DB
[ 80.0 ] [ °F ▼ ]

Indoor WB
[ 67.0 ] [ °F ▼ ]

Outdoor DB
[ 95.0 ] [ °F ▼ ]

Outdoor WB
[ 75.0 ] [ °F ▼ ]

Supported units:

- °F

- °C

- K

The professional should be able to use different units for different inputs.

# Internal Unit Handling

The application should use a single canonical internal unit system.

Recommended:

Kelvin (K) for temperature storage.

Example:

Professional Input
80°F
   ↓
Unit Conversion Engine
   ↓
Canonical Internal Value
   ↓
26.67°C / 299.82 K
   ↓
Display in selected unit

Do not store separate independent °F and °C values.

# DB/WB Validation

The application must validate the entering-air condition.

For normal atmospheric psychrometric conditions:

Wet-Bulb Temperature should not exceed Dry-Bulb Temperature.

### Valid

DB = 80°F
WB = 67°F

### Invalid

DB = 80°F
WB = 85°F

Display:

🔴 FAIL

The entered wet-bulb temperature is higher than the dry-bulb temperature. Check the entered condition and units.

The psychrometric engine should perform additional physical-validity checks.

# Psychrometric Calculations

Once DB/WB are established, calculate:

- Relative Humidity

- Dew Point

- Humidity Ratio

- Moist-Air Enthalpy

- Specific Volume

- Air Density

- Vapor Pressure

Example:

| Property | Value | Source |
| --- | --- | --- |
| DB | 80°F | 🟣 Standard |
| WB | 67°F | 🟣 Standard |
| RH | XX% | 🟢 Calculated |
| Dew Point | XX°F | 🟢 Calculated |
| Humidity Ratio | XX lb/lb | 🟢 Calculated |
| Enthalpy | XX Btu/lb | 🟢 Calculated |
| Density | XX lb/ft³ | 🟢 Calculated |

# “Why?” Function

Every recommended value should have:

Why?

Example:

Indoor DB: 80°F

Clicking Why? should show:

WHY THIS VALUE?

Standard:
AHRI XXXX

Edition:
XXXX

Rating Condition:
Standard Cooling

Equipment:
DX Air Handling Unit

Reason:
This condition is associated with the selected
equipment type and rating condition.

Source:
[View Source]

# “View Source” Function

The professional should be able to see the source used to establish the value.

Display:

Source Organization

Standard

Edition

Document

Page / Section

Source URL

Verification Status

Example:

🟢 Verified Source

or:

⚠ Review Required

# Source Classification

Every value must have a source classification.

### 🔵 PROFESSIONAL INPUT

Value directly entered by the professional.

### 🟣 STANDARD

Value obtained from an applicable standard.

### ⚫ MANUFACTURER DATA

Value obtained from manufacturer information.

### 🟢 CALCULATED

Value calculated by the application.

### 🟢 DERIVED

Value derived from another database relationship or calculation.

### 🟠 USER OVERRIDE

Value modified from the recommended value.

### ⚠ REVIEW REQUIRED

Value requiring professional/engineering review.

# Important Database Principle

The standard database must be data-driven, not code-driven.

Do NOT implement:

IF Product = AHU
THEN DB = 80°F
AND WB = 67°F

Instead:

Product Type
      +
Equipment Type
      +
Operating Mode
      +
Installation Location
      +
Market
      +
Climate
      +
Applicable Standard
      +
Standard Edition
      +
Rating Condition
            ↓
    STANDARD DATABASE
            ↓
     DB / WB VALUES
            ↓
  RECOMMENDED CONDITION

This allows the developer to add new standards without modifying the application’s core calculation code.

# 40. Standard Database Must Be Version Controlled

Every standard condition should have:

Standard
Edition
Revision
Effective Date
Status
Source
Verification Date
Verified By

Possible status:

- 🟢 Active

- 🟡 Pending Verification

- ⚠ Review Required

- ⚫ Superseded

- 🔴 Invalid

A project must retain the standard edition that was used when the project was created.

# 41. Refrigeration-Specific Consideration

Do not automatically apply air-conditioning DB/WB conditions to every refrigeration product.

For refrigeration applications, the required condition may instead include:

- Room DB

- Room RH

- Room WB

- Product temperature

- Product entering temperature

- Evaporator entering air

- Evaporator leaving air

- Ambient condition

- Condenser entering condition

- Process fluid condition

Therefore, the standard-condition database must support equipment-specific parameters.

The database architecture should be expandable beyond DB/WB.

# Future-Ready Condition Database

The developer should design the condition model so it can later support:

### Air Conditions

- DB

- WB

- RH

- Dew Point

- Humidity Ratio

- Enthalpy

### Outdoor Conditions

- Outdoor DB

- Outdoor WB

- Outdoor RH

- Design temperature

- Low ambient temperature

- High ambient temperature

### Water Conditions

- Entering Water Temperature

- Leaving Water Temperature

- Flow Rate

- ΔT

### Refrigeration Conditions

- Room Temperature

- Product Temperature

- Evaporating Temperature

- Condensing Temperature

- Superheat

- Subcooling

This prevents the Phase 1 database from becoming a dead-end architecture.

# 43. Final Recommended Screen

# Recommended Design Conditions

### Application

Product Type: Air Conditioning

Equipment: DX Air Handling Unit

Operating Mode: Cooling

Installation Location: Selected Location

Climate: Detected Climate

Applicable Standard: Selected Standard

Standard Edition: XXXX

Rating/Test Condition: Standard Cooling

## Entering Air

| Air Stream | DB (°F) | DB (°C) | WB (°F) | WB (°C) | Source |
| --- | --- | --- | --- | --- | --- |
| Indoor / Entering Air | 80.0 | 26.7 | 67.0 | 19.4 | 🟣 Standard |

## Outdoor Condition

| Air Stream | DB (°F) | DB (°C) | WB (°F) | WB (°C) | Source |
| --- | --- | --- | --- | --- | --- |
| Outdoor / Condenser Air | 95.0 | 35.0 | 75.0 | 23.9 | 🟣 Standard |

### Condition Status

🟣 STANDARD RECOMMENDATION

These conditions were selected from the applicable standard and rating condition associated with the selected product, equipment type, operating mode, location/market, and climate.

[ Accept Conditions ]

[ Modify Conditions ]

[ Why These Conditions? ]

[ View Source ]

# If Automatic Standard Retrieval Fails

The application must not stop functioning simply because an online standard source cannot be accessed.

Instead:

Attempt Automatic Retrieval
          ↓
       SUCCESS
          │
          ▼
     Use Verified Data


          OR


       FAILURE
          │
          ▼
Check Internal Standard Database
          │
          ▼
Find Matching Verified Record
          │
          ▼
Recommend Condition

If no verified database record exists:

⚠ REVIEW REQUIRED

A verified rating condition could not be automatically determined for this application. Please select a standard/rating condition or add/verify the required standard data in the Standards Database.

This is much safer than automatically guessing a DB/WB condition.

# 45. Complete Phase 1 Data Flow

PROFESSIONAL
                      │
                      ▼
                PRODUCT TYPE
                      │
                      ▼
               EQUIPMENT TYPE
                      │
                      ▼
                OPERATING MODE
                      │
                      ▼
          PRODUCT INSTALLATION LOCATION
                      │
                      ▼
                   CLIMATE
                      │
                      ▼
          STANDARD SELECTION ENGINE
                      │
              ┌───────┴────────┐
              │                │
        AUTO SOURCE       INTERNAL DB
              │                │
              └───────┬────────┘
                      ▼
             STANDARD CONDITION
                  DATABASE
                      │
                      ▼
              RATING CONDITION
                      │
                      ▼
             RECOMMENDED DB/WB
                      │
               ┌──────┴──────┐
               │             │
            ACCEPT         MODIFY
               │             │
               │             ▼
               │       PROFESSIONAL
               │         OVERRIDE
               │             │
               └──────┬──────┘
                      ▼
             PROJECT CONDITION
                      │
                      ▼
               VALIDATION ENGINE
                      │
                      ▼
             PSYCHROMETRIC ENGINE
                      │
                      ▼
       RH / DP / W / h / Density
                      │
                      ▼
              NEXT DESIGN STEP

# 46. Phase 1 Minimum Requirements

The first release must include:

### Application Selection

- Product Type

- Equipment Type

- Operating Mode

- Product Installation Location

- Climate

### Standards

- Applicable Standard Selection

- Standard Edition

- Rating/Test Condition

- Standard Database

- Source Reference

- Source Verification

- Standard Version Control

### Air Conditions

- Entering DB

- Entering WB

- Outdoor DB

- Outdoor WB where applicable

- °F / °C / K per-field unit selection