## Source Data
Equivalent Length of Pipe Fittings, Valve and Refrigeration Devices
Nominal Diameter | Fittings and Couplings (Feet) | [15 empty] | Valves & Refrigeration Devices (Feet)
| Elbow | [5 empty] | Tee |  |  |  | Coupling | [5 empty] | Ball valve | Globe / Solenoid | Angle Valve | Gate Valve | Swing Check | Sight Glass | Filter-Drier | Suction Filter
| 90° Elbow |  |  | 45° Elbow |  | 180° Elbow | Tee Branch | Tee Straight |  |  | Enlarging |  |  | Reducing | [10 empty] | Equivalent Length of EXV and Hot Gas Bypass Valve
| 90° Std | 90° Long Radius | 90° Street | 45° Std | 45° Street | 180° Std | Tee Branch Flow | Tee Straight (No Red.) | Tee Straight (25% Red.) | Tee Straight (50% Red.) | Enlarging 1/4 | Enlarging 1/2 | Enlarging 3/4 | Reducing 1/4 | Reducing 1/2 | Reducing 3/4 | [8 empty] | EXV Nominal ODF Size | Approx. Equivalent Length | HGB Valve Connection Size (ODF) | Approx. Equivalent Length
1/2 | 1.4 | 0.9 | 2.3 | 0.7 | 1.1 | 2.3 | 2.7 | 0.9 | 1.2 | 1.4 | 1.4 | 0.8 | 0.3 | 0.7 | 0.5 | 0.3 | 1.1 | 17 | 6 | 0.6 | 5 | 1 | 12 | 15 | ¼" ODF | 6–8 ft | ¼" ODF | 8–15 ft
5/8 | 1.6 | 1 | 2.5 | 0.8 | 1.3 | 2.5 | 3 | 1 | 1.4 | 1.6 | 1.8 | 1.1 | 0.4 | 0.9 | 0.7 | 0.4 | 0.9 | 18 | 7 | 0.7 | 6 | 1.2 | 15 | 17 | 5⁄16" ODF | 7–10 ft | 5⁄16" ODF | 10–18 ft
3/4 | 1.9 | 1.3 | — | 0.6 | — | — | 3 | 1.4 | 1.9 | 2 | 2.5 | 1.5 | 0.5 | 1.2 | 1 | 0.5 | 0.9 | 14 | 7 | — | 7 | 0.9 | — | — | ⅜" ODF | 8–12 ft | ⅜" ODF | 12–20 ft
7/8 | 2.3 | 1.5 | 3.2 | 0.9 | 1.6 | 3.2 | 4 | 1.7 | 2.2 | 2.6 | 3.2 | 2 | 0.7 | 1.6 | 1.2 | 0.7 | 0.9 | 22 | 9 | 0.9 | 8 | 1.6 | 21 | 22 | ½" ODF | 10–15 ft | ½" ODF | 15–25 ft
1-1/8 | 2.7 | 1.8 | 4.1 | 1.3 | 2.1 | 4.1 | 5 | 2.3 | 3.1 | 3.3 | 4.7 | 3 | 1 | 2.3 | 1.8 | 1 | 0.9 | 29 | 12 | 1 | 12 | 2 | 26 | 25 | ⅝" ODF | 12–20 ft | ⅝" ODF | 18–30 ft
1-3/8 | 3.6 | 2.4 | 5.6 | 1.7 | 3 | 5.6 | 7 | 2.6 | 3.7 | 4 | 5.8 | 3.6 | 1.2 | 2.9 | 2.2 | 1.2 | 1 | 38 | 15 | 1.5 | 15 | 2.5 | 35 | 36 | ¾" ODF | 15–22 ft | ¾" ODF | 20–35 ft
1-5/8 | 4.2 | 2.8 | 6.3 | 2.1 | 3.4 | 6.3 | 8 | 3.3 | 4.7 | 5 | 8 | 4.8 | 1.6 | 4 | 3 | 1.6 | 1.1 | 43 | 18 | 1.8 | 17 | 2.6 | — | 40 | ⅞" ODF | 18–26 ft | ⅞" ODF | 25–40 ft
2-1/8 | 5.9 | 3.9 | 8.2 | 2.6 | 4.5 | 8.2 | 10 | 4.1 | 5.6 | 6 | 10 | 6.1 | 2 | 5 | 3.8 | 2 | 1.2 | 55 | 24 | 2.3 | 22 | 3 | — | — | 1⅛" ODF | 20–30 ft | 1⅛" ODF | 30–50 ft
2-5/8 | 6.9 | 4.6 | 10 | 3.2 | 5.2 | 10 | 12 | 5 | 7 | 7.5 | 13 | 8 | 2.6 | 6.5 | 4.9 | 2.6 | 1.8 | 69 | 29 | 2.8 | 26 | 3.5 | — | — | 1⅜" ODF | 25–35 ft | 1⅜" ODF | 35–55 ft
3-1/8 | 7.7 | 5.5 | 12 | 4 | 6.4 | 12 | 15 | 5.9 | 8 | 9 | 15 | 9.2 | 3 | 7.7 | 6 | 3 | 2.5 | 84 | 35 | 3.2 | 34 | 4.5 | — | — | 1⅝" ODF | 30–40 ft | 1⅝" ODF | 40–65 ft
3-5/8 | 9.8 | 6.5 | 15 | 4.7 | 7.3 | 15 | 18 | 6.7 | 9 | 10 | 17 | 11 | 3.8 | 9 | 6.8 | 3.8 | 3.1 | 100 | 41 | 4 | 40 | 5 | — | —
4-1/8 | 10 | 6.7 | 17 | 5.2 | 8.5 | 17 | 21 | 8.2 | 12 | 13 | — | — | — | — | — | — | 3.8 | 120 | 47 | 4.5 | 40 | — | — | —
5-1/8 | 13 | 8.2 | 21 | 6.5 | 11 | 21 | 25 | 10 | 14 | 16 | — | — | — | — | — | — | 4.5 | 140 | 58 | 6 | 50 | — | — | —
6-1/8 | 16 | 10 | 25 | 7.9 | 13 | 25 | 30 | 13 | 18 | 20 | — | — | — | — | — | — | 5.2 | 170 | 70 | 7 | 60 | — | — | —
8-1/8 | 20 | 13 | — | 10 | — | 33 | 40 | — | — | — | — | — | — | — | — | — | 5.9 | 220 | 85 | 9 | 80 | — | — | —

## Equivalent Length
| Pipe 1 |  | Pipe 2 | Pipe 3 | Pipe 4 | Pipe 5 | Pipe 6 | Pipe 7 | Pipe 8 | Pipe 9 | Pipe 10 | Pipe 11
Pipe Length calculator | 7.5 |  | Pipe 2: 2.75; Pipe 3: 5.375
Total Pipe Length | 15.625
Line Type | Suction Lines- Compressor 1 & Compressor 2
Total Pipe Length | 103
Type of Fitting | Elbow 1(FXC) | Elbow 2(CXC) | Pipe 2: Reducer; Pipe 3: Ref Valve
| 90 Deg LR | 90 Deg LR | Pipe 2: FTC X C
Size | 1-3/8 | 1-3/8 | Pipe 2: 1-3/8 X 1-5/8; Pipe 3: 1-3/8
Equivalent Length of the Fitting | 28.8 | 28.8 | Pipe 2: 34.8; Pipe 3: 12
Quantity | 4 | 5 | bar: Pipe 2 to Pipe 3
Total Equivalent Length of the Fitting | 115.2 | 144 | Pipe 2: 34.8; Pipe 3: 12
Total Equivalent Length of line (in) | 409
Total Equivalent Length of line (ft) | 34.0833 | bar: Pipe 2 to Pipe 3
Total Equivalent Length of line (m) | 10.3886
Line Type | Suction Line 1 - Compressor 1
Total Pipe Length | 45
Type of Fitting | Elbow 1(FTCXC) |  | Pipe 3: Elbow 2(CXC); Pipe 4: Reducer; Pipe 5: Ref Valve
| 90 Deg LR |  | Pipe 3: 90 Deg LR; Pipe 4: FTC X C
Size | 1-3/8 |  | Pipe 3: 1-3/8; Pipe 4: 1-3/8 X 1-5/8; Pipe 5: 1-3/8
Equivalent Length of the Fitting | 28.8 |  | Pipe 3: 28.8; Pipe 4: 34.8; Pipe 5: 12
Quantity | 4 | bar: Pipe 3 to Pipe 5
Total Equivalent Length of the Fitting | 115.2 |  | Pipe 3: 28.8; Pipe 4: 34.8; Pipe 5: 12
Total Equivalent Length of line (in) | 235.8
Total Equivalent Length of line (ft) | 19.65 | [11 empty] | 2026-03-08 | 15 | 4 | bar: Pipe 2 to Pipe 5
Total Equivalent Length of line (m) | 5.9893
Line Type | Suction Line 2 - Compressor 2
Total Pipe Length | 58
Type of Fitting | Elbow 2( CXC) |  | Pipe 3: Ref Valve
90 Deg LR
Size | 1-3/8" |  | Pipe 3: 1-3/8
Equivalent Length of the Fitting | 28.8 |  | Pipe 3: 10.8
Quantity | 4 | bar: Pipe 3
Total Equivalent Length of the Fitting | 115.2 |  | Pipe 3: 10.8
Total Equivalent Length of line (in) | 184
Total Equivalent Length of line (ft) | 15.3333 | bar: Pipe 2 to Pipe 3
Total Equivalent Length of line (m) | 4.6736
Line Type | Discharge Lines- Compressor 1 & Compressor 2
Total Pipe Length | 80
Type of Fitting | Elbow 1 FTC X C | Elbow 2 cxc | Pipe 2: Tee 1( cxcxc)
| 90 Deg LR | 90 Deg LR | Pipe 2: Branch
Size | 1-1/8 | 1-1/8 | Pipe 2: 1-1/8
Equivalent Length of the Fitting | 21.6 | 21.6 | Pipe 2: 27.6
Quantity | 4 | 4 | Pipe 2: 2
Total Equivalent Length of the Fitting | 86.4 | 86.4 | Pipe 2: 55.2
Total Equivalent Length of line (in) | 308
Total Equivalent Length of line (ft) | 25.6667 | bar: Pipe 2
Total Equivalent Length of line (m) | 7.8232
Line Type | Discharge Line 1 - Compressor 1 (1-1/8)
Total Pipe Length | 45
Type of Fitting | Elbow 1 (F X C) | Tee | Pipe 2: Elbow 2
| 90 Deg LR | Branch | Pipe 2: 90 Deg LR
Size | 1-1/8 | 1-1/8 | Pipe 2: 1-1/8
Equivalent Length of the Fitting | 21.6 | 27.6 | Pipe 2: 21.6
Quantity | 2 | 1 | Pipe 2: 2
Total Equivalent Length of the Fitting | 43.2 | 27.6 | Pipe 2: 43.2
Total Equivalent Length of line (in) | 159
Total Equivalent Length of line (ft) | 13.25 | bar: Pipe 2
Total Equivalent Length of line (m) | 4.0386
Line Type | Discharge Line 2 - Compressor 2
Total Pipe Length | 35
Type of Fitting | Elbow 1(FXC) | Tee | Pipe 2: Elbow 2(CXC)
| 90 Deg LR | Branch | Pipe 2: 90 Deg LR
Size | 1-1/8 | 1-1/8 | Pipe 2: 1-1/8
Equivalent Length of the Fitting | 21.6 | 27.6 | Pipe 2: 21.6
Quantity | 2 | 1 | Pipe 2: 2
Total Equivalent Length of the Fitting | 43.2 | 27.6 | Pipe 2: 43.2
Total Equivalent Length of line (in) | 149
Total Equivalent Length of line (ft) | 12.4167 | bar: Pipe 2
Total Equivalent Length of line (m) | 3.7846
| Line Type | HGBV Line 1
| Total Pipe Length | 12
| Type of Fitting | Elbow 1 | Pipe 2: Reducer; Pipe 3: HGBV
|  | 90 Deg LR FXC | Pipe 2: FTC X C
| Size | 2026-05-08 | Pipe 2: 1-1/8 X 5/8; Pipe 3: 2026-05-08
| Equivalent Length of the Fitting | 12 | Pipe 2: 8.4; Pipe 3: 360
| Quantity | 1 | bar: Pipe 2 to Pipe 3
| Total Equivalent Length of the Fitting | 12 | Pipe 2: 8.4; Pipe 3: 360
| Total Equivalent Length of line (in) | 392.4
| Total Equivalent Length of line (ft) | 32.7 | bar: Pipe 2 to Pipe 3
| Total Equivalent Length of line (m) | 9.967
| Line Type | HGBV Line 2
| Total Pipe Length | 14
| Type of Fitting | Elbow 1( FXC) | Pipe 2: Reducer; Pipe 3: HGBV
|  | 90 Deg LR | Pipe 2: FTC X C
| Size | 2026-05-08 | Pipe 2: 1-1/8 X5/8; Pipe 3: 2026-05-08
| Equivalent Length of the Fitting | 12 | Pipe 2: 8.4; Pipe 3: 360
| Quantity | 1 | bar: Pipe 2 to Pipe 3
| Total Equivalent Length of the Fitting | 12 | Pipe 2: 8.4; Pipe 3: 360
| Total Equivalent Length of line (in) | 394.4
| Total Equivalent Length of line (ft) | 32.8667 | bar: Pipe 2 to Pipe 3
| Total Equivalent Length of line (m) | 10.0178
Line Type | Liquid Line 1- Compressor 1
Total Pipe Length | 52
Type of Fitting | Elbow 1 | Filter Drier | Pipe 2: Elbow 2(CXC); Pipe 3: Elbow 3 (FXC); Pipe 4: Ref Valve
| 90 Deg LR |  | Pipe 2: 90 Deg LR; Pipe 3: 90 Deg LR
Size | 7/8 | 7/8 | Pipe 2: 7/8; Pipe 3: 1-1/8; Pipe 4: 7/8
Equivalent Length of the Fitting | 18 | 21 | Pipe 2: 18; Pipe 3: 21.6; Pipe 4: 10.8
Quantity | 2 | 1 | Pipe 2: 5; Pipe 3: 1; Pipe 4: 1
Total Equivalent Length of the Fitting | 36 | 21 | Pipe 2: 90; Pipe 3: 21.6; Pipe 4: 10.8
Total Equivalent Length of line (in) | 231.4
Total Equivalent Length of line (ft) | 19.2833 | bar: Pipe 2
Total Equivalent Length of line (m) | 5.8776
Line Type | Liquid Line 2( A&B)- Compressor 2
Total Pipe Length | 87
Type of Fitting | Elbow 1 | Filter Drier | Pipe 2: Elbow 2(CXC); Pipe 3: Elbow 3 (FXC); Pipe 4: Ref Valve; Pipe 5: Reducer
| 90 Deg LR |  | Pipe 2: 90 Deg LR; Pipe 3: 90 Deg LR; Pipe 5: FTC X C
Size | 7/8 | 7/8 | Pipe 2: 7/8; Pipe 3: 1-1/8; Pipe 4: 7/8; Pipe 5: 1 1/8 X 7/8
Equivalent Length of the Fitting | 18 | 21 | Pipe 2: 18; Pipe 3: 21.6; Pipe 4: 10.8; Pipe 5: 19.2
Quantity | 1 | 1 | Pipe 2: 3; Pipe 3: 1; Pipe 4: 1; Pipe 5: 1
Total Equivalent Length of the Fitting | 18 | 1 | Pipe 2: 54; Pipe 3: 21.6; Pipe 4: 10.8; Pipe 5: 19.2
Total Equivalent Length of line (in) | 211.6
Total Equivalent Length of line (ft) | 17.6333 | bar: Pipe 2
Total Equivalent Length of line (m) | 5.3746